## Initial
WB/PI Calc-UTH® WATER AUDIT SOFTWARE IWA WB ASSESSMENT & PERFORMANCE INDICATORS
|  |  | version: | 2.2
2017
WATER UTILITY:
Relations
Variables
PIs
WB
DEVELOPED BY: |  | Dr. V. Kanakoudis & Dr. S. Tsitsifli |  |  | WB-1stMOD'
WB-2ndMOD'
Laboratory of Hydromechanics & Environmental Engineering Civil Engineering Department, University of Thessaly

## Relations
VARIABLES (ΜΕΤΑΒΛΗΤΕΣ)
|  |  | no of Variable | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 |  | no of Variable
| IWA PERFORMANCE INDICATORS - IWA PIs (ΔΕΙΚΤΕΣ ΠΡΟΣΔΙΟΡΙΣΜΟΥ ΤΟΥ ΕΠΙΠΕΔΟΥ ΛΕΙΤΟΥΡΓΙΑΣ ΤΟΥ ΔΙΚΤΥΟΥ) | no of PI |  | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | Α23 | Α24 | Α25 | Α26 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | B21 | B22 | B23 | B24 | B25 | B26 | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | C14 | C15 | C16 | C17 | C18 | C19 | C20 | C21 | C22 | C23 | C24 | C25 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10 | D11 | D12 | D13 | D14 | D15 | D16 | D17 | D18 | D19 | D20 | D21 | D22 | D23 | D24 | D25 | D26 | D27 | D28 | D29 | D30 | D31 | D32 | D33 | D34 | D35 | D36 | D37 | D38 | D39 | D40 | D41 | D42 | D43 | D44 | D45 | D46 | D47 | D48 | D49 | D50 | D51 | D52 | D53 | D54 | D55 | D56 | D57 | D58 | D59 | D60 | D61 | D62 | D63 | D64 | D65 | Ε1 | Ε2 | Ε3 | Ε4 | Ε5 | Ε6 | Ε7 | Ε8 | Ε9 | Ε10 | Ε11 | F1 | F2 | F3 | F4 | F5 | F6 | F7 | F8 | F9 | F10 | F11 | F12 | F13 | F14 | F15 | F16 | F17 | F18 | F19 | F20 | F21 | F22 | F23 | G1 | G2 | G3 | G4 | G5 | G6 | G7 | G8 | G9 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G24 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | G41 | G42 | G43 | G44 | G45 | G46 | G47 | G48 | G49 | G50 | G51 | G52 | G53 | G54 | G55 | G56 | G57 | G58 | H1 | H2 | 429 |  | no of PI | IWA PERFORMANCE INDICATORS - IWA PIs (ΔΕΙΚΤΕΣ ΠΡΟΣΔΙΟΡΙΣΜΟΥ ΤΟΥ ΕΠΙΠΕΔΟΥ ΛΕΙΤΟΥΡΓΙΑΣ ΤΟΥ ΔΙΚΤΥΟΥ) | no of PI
2 |  | 1 | WR1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 19 A19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | WR1 | 1 |  | 1
4 |  | 2 | WR2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 1 A1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 2 A2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 4 | WR2 | 2 |  | 2
3 |  | 3 | WR3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 1 A1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | WR3 | 3 |  | 3
2 |  | 4 | WR4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 22 A22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | WR4 | 4 |  | 4
2 |  | 5 | Pe1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe1 | 5 |  | 5
3 |  | 6 | Pe2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 6 A6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe2 | 6 |  | 6
2 |  | 7 | Pe3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 28 B2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe3 | 7 |  | 7
2 |  | 8 | Pe4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 29 B3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe4 | 8 |  | 8
2 |  | 9 | Pe5 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 30 B4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe5 | 9 |  | 9
2 |  | 10 | Pe6 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 31 B5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe6 | 10 |  | 10
2 |  | 11 | Pe7 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 32 B6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe7 | 11 |  | 11
2 |  | 12 | Pe8 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 33 B7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe8 | 12 |  | 12
2 |  | 13 | Pe9 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 34 B8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe9 | 13 |  | 13
3 |  | 14 | Pe10 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 6 A6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 35 B9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe10 | 14 |  | 14
3 |  | 15 | Pe11 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 6 A6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 36 B10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe11 | 15 |  | 15
2 |  | 16 | Pe12 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 37 B11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe12 | 16 |  | 16
3 |  | 17 | Pe13 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 38 B12: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 129 D52: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe13 | 17 |  | 17
3 |  | 18 | Pe14 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 39 B13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 62 C10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 148 Ε6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe14 | 18 |  | 18
2 |  | 19 | Pe15 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 32 B6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 40 B14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe15 | 19 |  | 19
2 |  | 20 | Pe16 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 41 B15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe16 | 20 |  | 20
2 |  | 21 | Pe17 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 42 B16: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe17 | 21 |  | 21
2 |  | 22 | Pe18 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 43 B17: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe18 | 22 |  | 22
3 |  | 23 | Pe19 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 44 B18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe19 | 23 |  | 23
3 |  | 24 | Pe20 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 45 B19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe20 | 24 |  | 24
3 |  | 25 | Pe21 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 46 B20: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe21 | 25 |  | 25
3 |  | 26 | Pe22 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 47 B21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe22 | 26 |  | 26
3 |  | 27 | Pe23 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 48 B22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe23 | 27 |  | 27
3 |  | 28 | Pe24 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 49 B23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe24 | 28 |  | 28
3 |  | 29 | Pe25 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 27 B1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 50 B24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Pe25 | 29 |  | 29
2 |  | 30 | Pe26 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 51 B25: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 52 B26: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Pe26 | 30 |  | 30
2 |  | 31 | Ph1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 4 A4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 55 C3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph1 | 31 |  | 31
3 |  | 32 | Ph2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 53 C1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Ph2 | 32 |  | 32
3 |  | 33 | Ph3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 54 C2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Ph3 | 33 |  | 33
2 |  | 34 | Ph4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 59 C7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 79 D2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph4 | 34 |  | 34
2 |  | 35 | Ph5 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 78 D1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 80 D3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph5 | 35 |  | 35
2 |  | 36 | Ph6 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 78 D1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 81 D4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph6 | 36 |  | 36
2 |  | 37 | Ph7 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 78 D1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 82 D5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph7 | 37 |  | 37
2 |  | 38 | Ph8 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 61 C9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 74 C22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph8 | 38 |  | 38
2 |  | 39 | Ph9 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 61 C9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 75 C23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph9 | 39 |  | 39
2 |  | 40 | Ph10 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 63 C11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph10 | 40 |  | 40
2 |  | 41 | Ph11 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 148 Ε6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph11 | 41 |  | 41
3 |  | 42 | Ph12 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 148 Ε6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 151 Ε9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 152 Ε10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Ph12 | 42 |  | 42
2 |  | 43 | Ph13 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 149 Ε7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 153 Ε11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph13 | 43 |  | 43
2 |  | 44 | Ph14 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 67 C15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 68 C16: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph14 | 44 |  | 44
2 |  | 45 | Ph15 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 67 C15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 69 C17: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Ph15 | 45 |  | 45
3 |  | 46 | Op1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 58 C6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 83 D6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op1 | 46 |  | 46
3 |  | 47 | Op2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 54 C2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 84 D7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op2 | 47 |  | 47
3 |  | 48 | Op3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 85 D8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op3 | 48 |  | 48
3 |  | 49 | Op4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 86 D9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op4 | 49 |  | 49
3 |  | 50 | Op5 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 87 D10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op5 | 50 |  | 50
3 |  | 51 | Op6 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 75 C23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 88 D11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op6 | 51 |  | 51
3 |  | 52 | Op7 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 62 C10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 89 D12: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op7 | 52 |  | 52
3 |  | 53 | Op8 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 122 D45: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 148 Ε6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op8 | 53 |  | 53
3 |  | 54 | Op9 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 64 C12: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 90 D13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op9 | 54 |  | 54
3 |  | 55 | Op10 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 65 C13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 91 D14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op10 | 55 |  | 55
3 |  | 56 | Op11 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 66 C14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 92 D15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op11 | 56 |  | 56
3 |  | 57 | Op12 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 70 C18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 93 D16: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op12 | 57 |  | 57
3 |  | 58 | Op13 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 71 C19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 94 D17: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op13 | 58 |  | 58
3 |  | 59 | Op14 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 72 C20: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 95 D18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op14 | 59 |  | 59
2 |  | 60 | Op15 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 96 D19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op15 | 60 |  | 60
3 |  | 61 | Op16 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 97 D20: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op16 | 61 |  | 61
3 |  | 62 | Op17 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 98 D21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op17 | 62 |  | 62
3 |  | 63 | Op18 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 99 D22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op18 | 63 |  | 63
3 |  | 64 | Op19 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 73 C21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 100 D23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op19 | 64 |  | 64
3 |  | 65 | Op20 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 101 D24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op20 | 65 |  | 65
3 |  | 66 | Op21 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 58 C6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 102 D25: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op21 | 66 |  | 66
3 |  | 67 | Op22 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 58 C6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 103 D26: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op22 | 67 |  | 67
3 |  | 68 | Op23 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 15 A15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op23 | 68 |  | 68
3 |  | 69 | Op24 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 15 A15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op24 | 69 |  | 69
4 |  | 70 | Op25 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 5 A5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 7 A7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 18 A18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 4 | Op25 | 70 |  | 70
2 |  | 71 | Op26 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 18 A18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op26 | 71 |  | 71
3 |  | 72 | Op27 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 19 A19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 H2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op27 | 72 |  | 72
3 |  | 73 | Op28 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 19 A19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 H2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op28 | 73 |  | 73
4 |  | 74 | Op29 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 77 C25: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 111 D34: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 4 | Op29 | 74 |  | 74
3 |  | 75 | Op30 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 56 C4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 104 D27: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op30 | 75 |  | 75
3 |  | 76 | Op31 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 60 C8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 105 D28: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op31 | 76 |  | 76
3 |  | 77 | Op32 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 106 D29: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op32 | 77 |  | 77
3 |  | 78 | Op33 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 75 C23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 107 D30: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op33 | 78 |  | 78
3 |  | 79 | Op34 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 57 C5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 108 D31: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op34 | 79 |  | 79
3 |  | 80 | Op35 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 109 D32: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 159 F6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op35 | 80 |  | 80
8 |  | 81 | Op36 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 116 D39: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 117 D40: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 118 D41: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 119 D42: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 149 Ε7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 150 Ε8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 151 Ε9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 8 | Op36 | 81 |  | 81
4 |  | 82 | Op37 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 116 D39: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 120 D43: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 149 Ε7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 4 | Op37 | 82 |  | 82
2 |  | 83 | Op38 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 121 D44: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 148 Ε6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op38 | 83 |  | 83
3 |  | 84 | Op39 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 8 A8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 11 A11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Op39 | 84 |  | 84
2 |  | 85 | Op40 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 123 D46: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 134 D57: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op40 | 85 |  | 85
2 |  | 86 | Op41 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 124 D47: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 135 D58: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op41 | 86 |  | 86
2 |  | 87 | Op42 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 125 D48: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 136 D59: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op42 | 87 |  | 87
2 |  | 88 | Op43 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 126 D49: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 137 D60: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op43 | 88 |  | 88
2 |  | 89 | Op44 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 127 D50: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 138 D61: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Op44 | 89 |  | 89
2 |  | 90 | QS1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 143 Ε1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 145 Ε3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS1 | 90 |  | 90
2 |  | 91 | QS2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 144 Ε2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 146 Ε4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS2 | 91 |  | 91
2 |  | 92 | QS3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 147 Ε5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 154 F1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS3 | 92 |  | 92
2 |  | 93 | QS4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 147 Ε5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 155 F2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS4 | 93 |  | 93
2 |  | 94 | QS5 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 147 Ε5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 156 F3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS5 | 94 |  | 94
2 |  | 95 | QS6 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 159 F6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 160 F7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS6 | 95 |  | 95
2 |  | 96 | QS7 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 157 F4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 159 F6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS7 | 96 |  | 96
3 |  | 97 | QS8 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 156 F3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 158 F5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS8 | 97 |  | 97
2 |  | 98 | QS9 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 156 F3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 161 F8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS9 | 98 |  | 98
2 |  | 99 | QS10 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 110 D33: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS10 | 99 |  | 99
2 |  | 100 | QS11 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 110 D33: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 151 Ε9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS11 | 100 |  | 100
2 |  | 101 | QS12 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 H2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS12 | 101 |  | 101
3 |  | 102 | QS13 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 112 D35: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 154 F1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS13 | 102 |  | 102
3 |  | 103 | QS14 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 113 D36: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS14 | 103 |  | 103
3 |  | 104 | QS15 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 113 D36: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 151 Ε9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS15 | 104 |  | 104
3 |  | 105 | QS16 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 114 D37: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 154 F1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS16 | 105 |  | 105
2 |  | 106 | QS17 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 115 D38: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS17 | 106 |  | 106
5 |  | 107 | QS18 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 128 D51: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 139 D62: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 140 D63: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 141 D64: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 142 D65: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 5 | QS18 | 107 |  | 107
2 |  | 108 | QS19 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 130 D53: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 139 D62: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS19 | 108 |  | 108
2 |  | 109 | QS20 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 131 D54: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 140 D63: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS20 | 109 |  | 109
2 |  | 110 | QS21 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 132 D55: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 141 D64: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS21 | 110 |  | 110
2 |  | 111 | QS22 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 133 D56: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 142 D65: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS22 | 111 |  | 111
2 |  | 112 | QS23 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 162 F9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 163 F10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS23 | 112 |  | 112
2 |  | 113 | QS24 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 164 F11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 165 F12: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS24 | 113 |  | 113
2 |  | 114 | QS25 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 166 F13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 167 F14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS25 | 114 |  | 114
3 |  | 115 | QS26 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 76 C24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS26 | 115 |  | 115
3 |  | 116 | QS27 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 152 Ε10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS27 | 116 |  | 116
2 |  | 117 | QS28 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 169 F16: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS28 | 117 |  | 117
2 |  | 118 | QS29 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 170 F17: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS29 | 118 |  | 118
2 |  | 119 | QS30 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 171 F18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS30 | 119 |  | 119
2 |  | 120 | QS31 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 168 F15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 172 F19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS31 | 120 |  | 120
3 |  | 121 | QS32 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 152 Ε10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 173 F20: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS32 | 121 |  | 121
3 |  | 122 | QS33 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 152 Ε10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 174 F21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | QS33 | 122 |  | 122
2 |  | 123 | QS34 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 175 F22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 176 F23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | QS34 | 123 |  | 123
3 |  | 124 | Fi1 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 178 G2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 211 G35: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi1 | 124 |  | 124
2 |  | 125 | Fi2 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 177 G1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 179 G3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi2 | 125 |  | 125
2 |  | 126 | Fi3 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 177 G1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 179 G3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi3 | 126 |  | 126
2 |  | 127 | Fi4 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 180 G4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi4 | 127 |  | 127
2 |  | 128 | Fi5 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi5 | 128 |  | 128
2 |  | 129 | Fi6 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 182 G6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi6 | 129 |  | 129
2 |  | 130 | Fi7 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 184 G8: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi7 | 130 |  | 130
2 |  | 131 | Fi8 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 185 G9: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi8 | 131 |  | 131
2 |  | 132 | Fi9 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 186 G10: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi9 | 132 |  | 132
2 |  | 133 | Fi10 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 187 G11: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi10 | 133 |  | 133
6 |  | 134 | Fi11 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 188 G12: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 189 G13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 190 G14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 191 G15: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 192 G16: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 6 | Fi11 | 134 |  | 134
2 |  | 135 | Fi12 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 193 G17: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi12 | 135 |  | 135
2 |  | 136 | Fi13 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 194 G18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi13 | 136 |  | 136
2 |  | 137 | Fi14 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 195 G19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi14 | 137 |  | 137
2 |  | 138 | Fi15 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 196 G20: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi15 | 138 |  | 138
2 |  | 139 | Fi16 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 197 G21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi16 | 139 |  | 139
2 |  | 140 | Fi17 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 198 G22: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi17 | 140 |  | 140
2 |  | 141 | Fi18 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 199 G23: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi18 | 141 |  | 141
2 |  | 142 | Fi19 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 200 G24: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi19 | 142 |  | 142
2 |  | 143 | Fi20 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 201 G25: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi20 | 143 |  | 143
2 |  | 144 | Fi21 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 202 G26: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi21 | 144 |  | 144
2 |  | 145 | Fi22 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 203 G27: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi22 | 145 |  | 145
2 |  | 146 | Fi23 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 182 G6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 204 G28: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi23 | 146 |  | 146
3 |  | 147 | Fi24 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 182 G6: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 205 G29: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 206 G30: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi24 | 147 |  | 147
2 |  | 148 | Fi25 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 208 G32: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi25 | 148 |  | 148
2 |  | 149 | Fi26 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 208 G32: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 209 G33: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi26 | 149 |  | 149
2 |  | 150 | Fi27 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 208 G32: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 210 G34: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi27 | 150 |  | 150
3 |  | 151 | Fi28 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 7 A7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 14 A14: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 212 G36: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi28 | 151 |  | 151
3 |  | 152 | Fi29 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 5 A5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 7 A7: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 213 G37: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi29 | 152 |  | 152
2 |  | 153 | Fi30 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 177 G1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 180 G4: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi30 | 153 |  | 153
2 |  | 154 | Fi31 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 177 G1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi31 | 154 |  | 154
3 |  | 155 | Fi32 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 179 G3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 214 G38: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 235 H1: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi32 | 155 |  | 155
2 |  | 156 | Fi33 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 204 G28: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 215 G39: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi33 | 156 |  | 156
2 |  | 157 | Fi34 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 208 G32: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 216 G40: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi34 | 157 |  | 157
2 |  | 158 | Fi35 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 217 G41: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 218 G42: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi35 | 158 |  | 158
2 |  | 159 | Fi36 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 204 G28: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 218 G42: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi36 | 159 |  | 159
2 |  | 160 | Fi37 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 219 G43: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 220 G44: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi37 | 160 |  | 160
2 |  | 161 | Fi38 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 178 G2: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 227 G51: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi38 | 161 |  | 161
2 |  | 162 | Fi39 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 221 G45: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 222 G46: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi39 | 162 |  | 162
2 |  | 163 | Fi40 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 223 G47: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 224 G48: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi40 | 163 |  | 163
2 |  | 164 | Fi41 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 225 G49: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 229 G53: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi41 | 164 |  | 164
3 |  | 165 | Fi42 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 217 G41: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 218 G42: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 230 G54: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi42 | 165 |  | 165
2 |  | 166 | Fi43 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 224 G48: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 232 G56: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi43 | 166 |  | 166
3 |  | 167 | Fi44 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 226 G50: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 230 G54: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 231 G55: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 3 | Fi44 | 167 |  | 167
2 |  | 168 | Fi45 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 179 G3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 226 G50: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi45 | 168 |  | 168
2 |  | 169 | Fi46 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 3 A3: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 21 A21: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 2 | Fi46 | 169 |  | 169
6 |  | 170 | Fi47 | VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 13 A13: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 18 A18: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 19 A19: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 181 G5: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 233 G57: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 234 G58: 1; VARIABLES (ΜΕΤΑΒΛΗΤΕΣ) 236 429: 6 | Fi47 | 170 |  | 170
429 |  |  | 429 | 2 | 1 | 10 | 1 | 2 | 3 | 3 | 1 | 0 | 0 | 1 | 0 | 1 | 6 | 2 | 0 | 0 | 3 | 4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 19 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 12 | 2 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 11 | 1 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 3 | 5 | 3 | 1 | 4 | 4 | 1 | 3 | 1 | 3 | 1 | 1 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | 4 | 2 | 19 | 3 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 1 | 1 | 0 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 1 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 58 | 3
|  |  |  | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | A9 | A10 | A11 | A12 | A13 | A14 | A15 | A16 | A17 | A18 | A19 | A20 | A21 | A22 | Α23 | Α24 | Α25 | Α26 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | B9 | B10 | B11 | B12 | B13 | B14 | B15 | B16 | B17 | B18 | B19 | B20 | B21 | B22 | B23 | B24 | B25 | B26 | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | C14 | C15 | C16 | C17 | C18 | C19 | C20 | C21 | C22 | C23 | C24 | C25 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | D9 | D10 | D11 | D12 | D13 | D14 | D15 | D16 | D17 | D18 | D19 | D20 | D21 | D22 | D23 | D24 | D25 | D26 | D27 | D28 | D29 | D30 | D31 | D32 | D33 | D34 | D35 | D36 | D37 | D38 | D39 | D40 | D41 | D42 | D43 | D44 | D45 | D46 | D47 | D48 | D49 | D50 | D51 | D52 | D53 | D54 | D55 | D56 | D57 | D58 | D59 | D60 | D61 | D62 | D63 | D64 | D65 | Ε1 | Ε2 | Ε3 | Ε4 | Ε5 | Ε6 | Ε7 | Ε8 | Ε9 | Ε10 | Ε11 | F1 | F2 | F3 | F4 | F5 | F6 | F7 | F8 | F9 | F10 | F11 | F12 | F13 | F14 | F15 | F16 | F17 | F18 | F19 | F20 | F21 | F22 | F23 | G1 | G2 | G3 | G4 | G5 | G6 | G7 | G8 | G9 | G10 | G11 | G12 | G13 | G14 | G15 | G16 | G17 | G18 | G19 | G20 | G21 | G22 | G23 | G24 | G25 | G26 | G27 | G28 | G29 | G30 | G31 | G32 | G33 | G34 | G35 | G36 | G37 | G38 | G39 | G40 | G41 | G42 | G43 | G44 | G45 | G46 | G47 | G48 | G49 | G50 | G51 | G52 | G53 | G54 | G55 | G56 | G57 | G58 | H1 | H2 | 0 |  | no of PI |  | no of PI
|  |  | no of Variable | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 |  | no of Variable

## Variables
Α/Α | VARIABLE | MEANING | VALUE | MEASURED IN | COMMENTS
Α1 | Annual yield capacity of own resources | Maximum annual volume of water that can potentially be abstracted from own resources, based on the availability of water resources and on any legal or contractual constraints |  | m3/year
Α2 | Annual imported water allowance | Maximum alloawance of raw and treated water importation |  | m3/year
Α3 | System input volume | The water volume input of the global system during the assessment period |  | m3
Α4 | Maximum water treated daily | Maximun daily volume of water treated in treated plans during the assessment period |  | m3/day
Α5 | Exporter raw water | Total volume of raw water transferred to other water undertaking or to another system from the same supply area during the assessment period |  | m3
Α6 | Water produced | Total volume of water treated for input to water transmission lines or derectly to the distribution system during the assessment period |  | m3
Α7 | Exported treated water | Total volume of treated water exported to other water undertaking or to another system from the same supply area during the assessment period |  | m3
Α8 | Billed metered consumption | Total amount of billed metered authorised consumption (including exported water) during the assessment period |  | m3
Α9 | Billed unmetered consumption | Total amount of billed unmetered authorised consumption (including exported water) during the assessment period | 0 | m3
Α10 | Billed authorised consumption | Total amount of billed authorised consumption (including exported water) during the assessment period | 0 | m3
Α11 | Unbilled metered consumption | Total amount of unbilled metered authorised consumption (including exported water) during the assessment period |  | m3
Α12 | Unbilled unmetered consumption | Total amount of unbilled unmetered authorised consumption (including exported water) during the assessment period |  | m3
Α13 | Unbilled authorised consumption | Total amount of unbilled authorised consumption (including exported water) during the assessment period | 0 | m3
Α14 | Authorised consumption | Total volume of metered and/or non-metered water that, during the assessment period, is taken by registered customers, by the water supplier itself, or by others who are implicitly authorised to do by the water supplier, for residential, commercial, industrial or public purposes. It includes water exported. | 0 | m3
Α15 | Water losses | Difference between system input volume and authorised consumption | 0 | m3
Α16 | Unauthorised cosnumption | Total amount of unauthorised water consumption during the assessment period, including water theft. |  | m3
Α17 | Metering inaccuracies water losses | Total amount of water consumed during the assessment period, but unccounted-for due to metering inaccuranies |  | m3
Α18 | Apparent losses | Total amount of water unaccounted-for due to unauthorised consumption and metering inaccurancies, durind the assessment period | 0 | m3
Α19 | Real losses | Total amount of physical water losses from the pressurised system during the assessment period, up to the point of costomer metering | 0 | m3
Α20 | Revenue water | Total amount of billed authorised consumption (including exported water) during the assessment period. | 0 | m3
Α21 | Non-revenue water | Difference between the system input volume and the billed authorised consumption (including exported water) during the assessment period. | 0 | m3
Α22 | Reused supplied water | Total volume of wastewater directly reused as water source during the assessment period, after adequate treatment, generally as a complement of conventional water sources. |  | m3
A23 | Non Recoverd Water | Water volume billed but never paid by the consumers |  | m3
A24 | Free Basic Recover Revenue | Difference between Revenue Water and Non Recovered Water | 0 | m3
Α25 | Minimum Charge Difference - MCD (Recovered Real Losses) | Difference between water volume billed to the customers and water volume registered by their water meters |  | m3
A26 | Accounted Non Revenue Water | Difference between NRW and MCD | 0 | m3
Β1 | Total personnel | Total number of full time equivalent employees of the water undertaking as the reference date. | 0 | Νο.
Β2 | General management personnel | Total number of full time equivalent employees dedicated to directorate, central administration, environmental management, new business development and general computing support at the reference date. |  | Νο.
Β3 | Human resources management personnel | Total number of full time equivalent employees of the water undertaking dedicated to personnel administration, education and trainig, occupational safety, and health services and social activities, at the reference date. |  | Νο.
Β4 | Financial and commercial personnel | Total number of full time equivalent employees of the water undertaking dedicated to economic and financial planning, economic administration, economic controlling and purchasing and material management activities, at the reference date. |  | Νο.
Β5 | Customer service personnel | Total number of full time equivalent employees dedicated to accounting and control and to customer relations and management activities, at the reference date. |  | Νο.
Β6 | Technical services personnel | Total number of full time equivalent employees dedicated to planning, construction, operations and maintenance activities, at the reference date. | 0 | Νο.
Β7 | Planning and construction personnel | Total number of full time equivalent employees of technical services working in planning & construction of water supply systems, at the reference date. |  | Νο.
Β8 | Operations and maintenance personnel | Total number of full time equivalent employees of technical services working in operations & maintenance of water supply systems, at the reference date. |  | Νο.
Β9 | Water resources and catchment management personnel | Total number of full time equivalent employees working in the water resources and catchment management, at the reference date. |  | Νο.
Β10 | Abstraction and treatment personnel | Total number of full time equivalent employees working in the planning, design, construction, operations and maintenance of the water abstraction and treatment, at the reference date. |  | Νο.
Β11 | Transmission, storage and distribution personnel | Total number of full time equivalent employees working in the planning, design, construction, operations and maintenance of the transmission, storage and distribution system, at the reference date. |  | Νο.
Β12 | Water quality monitoring personnel | Total number of full time equivalent employees working in water quality sampling and testing, at the reference date. |  | Νο.
Β13 | Meter management personnel | Total number of full time equivalent employees working in the installation, maintenance and replacement of the water meters, at the reference date. |  | Νο.
Β14 | Support services personnel | Total number of full time equivalent employees working in thecentral stock repository, central workshops and the vehicle fleet, at the reference date. |  | Νο.
Β15 | University degree personnel | Number of full time equivalent employees of the water undertaking with university degree, at the reference date. |  | Νο.
Β16 | Basic education personnel | Total number of full time equivalent employees working of the water undertaking without a university degree but with at least a basic education, at the reference date. |  | Νο.
Β17 | Other qualification personnel | Total number of full time equivalent employees without basic education, at the reference date. | 0 | Νο.
Β18 | Total training time | Total number of training hours during the assessment period. | 0 | hours
Β19 | Internal training time | Total number of internal training hours during the assessment period. |  | hours
Β20 | External training time | Total number of external training hours during the assessment period. |  | hours
Β21 | Working accidents | Total number of working accidents requiring care occurring with personnel during the assessment period |  | Νο.
Β22 | Absebteeism | Total number of days of absenteeism occuring during the assessment period | 0 | days
Β23 | Absenteeism due to accidents or illness at work | Total number of days of absenteeism due to accidents or illnes at work occuring during the assessment period |  | days
Β24 | Absedeeism due to other reasons | Total number of days of absenteeism occuring during the assessment period that were not due to working accidents or illness at work. |  | days
Β25 | Working time | Total number of normal working hours of all the undertaking employees during the assessment period (employees hours gross - absence for holidays) |  | hours
Β26 | Overtime work | Total number of overtime working hours of the undertaking employees during the assessment period. |  | hours
C1 | Raw water storage capacity | Total net volume of raw water reservoirs included in the system, at the reference date. |  | m3
C2 | Treated water storage capacity | Total volume of transmission and distribution service reservoirs, at the reference date. |  | m3
C3 | Daily treatment capacity | Maximum daily global capacity of the existing treatment plants, at the reference date. |  | m3/day
C4 | Pumps | Total number of pumps of the system, at the reference date. |  | Νο.
C5 | Pumping stations | Total number of pumping stations of the system (customer pumping systems excluded), at the reference date. |  | Νο.
C6 | Pumping stations capacity | Total nominal power of the system pumps (customer pumping systems excluded), at the reference date. |  | kW
C7 | Maximum operating pumping capacity | Maximum nominal pumping power that can be used simultaneously in the system. |  | kW
C8 | Mains length | Total transmission and distribution mains length (service connections not included), at the reference date. |  | km
C9 | Distribution mains length | Total distribution mains legth ( transmission lines and service connections not included), at the reference date. |  | km
C10 | System flow meters | Total number of flow meters available for permanentor temporary installation in the trasmission and distribution system, such as meters for system control, district metering and accounting of imported and exported water (direct customer meters, E6, shall not be included). |  | Νο.
C11 | District meters | Total number of water metering points permanently or systematically equipped for district metering, at the reference date. |  | Νο.
C12 | Pressure meters | Total number of pressure meters available for permanet or temporary pressure monitoring, at the reference date. |  | Νο.
C13 | Water level meters | Total number of water level meters available for permanent or temporary water level monitoring, at the reference date. |  | Νο.
C14 | On-line water quality monitoring instruments | Total number of instruments available for permanent or temporary on-line water quality monitoring, at the reference date. |  | Νο.
C15 | Control units | Total number of control units, defined as functionally independent sets of control devices of the system (e.g. control valves or pump switches) used in water wells, surface water catchments, pumping stations, energy recovery stations, treatment plants, storage tanks and raw water, transmission and distribution networks (at the reference date). |  | Νο.
C16 | Automated control units | Total number of automated control units of the system, defined as functionally independent sets of control devices of the system (e.g. control valves or pump switches) that are locally controlled by a programmable logical controller, used in water wells, surface water catchments, pumping stations, energy recovery stations, treatment plants, storage tanks and raw water, transmission and distribution networks (at the reference date). |  | Νο.
C17 | Remotely controlled units | Total number of control units of the system remotely controled from a central control system, usually via information cabling or radio connections, used in water wells, surface water catchments, pumping stations, energy recovery stations, treatment plants, storage tanks and raw water, transmission and distribution networks (at the reference date). |  | Νο.
C18 | Emergency power systems | Total nominal power of the emergency power systems, at the reference date. |  | kW
C19 | Signal transmission equipment | Total nominal of signal transmission units, at the reference date. |  | Νο.
C20 | Electrical switchgear | Total number of the electrical switchgear equipments, at the reference date. |  | Νο.
C21 | Mains valves | Total number of all kinds of valves installed in transmission and distribution system mains (valves installed in the service connections shall not be accounted for), at the reference date. |  | Νο.
C22 | Isolating valves | Total number of isolating valves of all types installed in transmission and distribution system mains (valves installed in the service connections shall not be accounted for), at the reference date. |  | Νο.
C23 | Hydrants | Total number of hydrants of all types installed in the distribution network, at the reference date. |  | Νο.
C24 | Service connections | Total number of service connections, at the reference date. |  | Νο.
C25 | Average service connection length | Average length (metres) from the property boundary (delivery point) to the measurement point, at the reference date. |  | m
D1 | Pumping energy consumption | Total energy consumption for water pumping (customer pumping systems excluded) during the assessment period. |  | kWh
D2 | Maximum daily pumping energy consumption | Sum, for all installed pumps, of the number of operation hours of the maximum energy consumption day during the assessment period multiplied by the nominal power of the pump, resulting in the maximum daily pumping energy consumption of the system. |  | kWh
D3 | Standardisation factor | Sum of D3(i) for all pumps of the system, D3(i) being: D3(i)=V(i)xh(i)/100, where V is the total volume (m3) pumped I during the assessment period and h(i) is the pump head (m). |  | m3*100m
D4 | Reactive energy consumption | Total reactive energy consumption for pumping in the system during the assessment period. |  | kVar
D5 | Energy recovery | Total energy recovered by the use of turbines or reverse pumps in the system during the assessment period. |  | Wh
D6 | Pumping inspection | Sum of the nominal power of all pumps and related ancillaries in the system subjected to inspection during the assessment period |  | kW
D7 | Storage tank cleaning | Total volume of water storage tanks cells cleaned during the assessment period. |  | m3
D8 | Network inspection | Length of transmission and distribution mains where at least valves and other fittings were inspected during the assessment period |  | km
D9 | Leakage control | Length of mains subject to active leakage control during the assessment period. |  | km
D10 | Leaks repaired due to active leakage control | Number of leaks detected and repaired due to active leakage control during the assessment period. |  | Νο.
D11 | Hydrant inspection | Total number of hydrants inspected during the assessment period. |  | Νο.
D12 | System flow meter calibrations | Number of system flowmeter calibrations carried out during the assessment period. |  | Νο.
D13 | Pressure meter calibrations | Number of pressure meter calibrations carried out during the assessment period. |  | Νο.
D14 | Water level meter calibrations | Number of water level meter calibrations carried out during the assessment period. |  | Νο.
D15 | On-line water quality monitoring equipment calibrations | Number of calibrations carried out during the assessment period on on-line water quality monitoring instruments installed in the system (permanently or temporarily) |  | Νο.
D16 | Emergency power systems inspection | Sum of the nominal power of the system emergency power equipment inspected during the assessment period. |  | kW
D17 | Signal transmission equipment inspection | Number of signal transmission units in the system inspected during the assessment period |  | Νο.
D18 | Electrical switchgear inspection | Number of electrical switchgear units in the system inspected during the assessment period |  | Νο.
D19 | Permanent vehicles | Number of permanent vehicles daily available, in average, for field works in operations and maintenance activities, at the reference date. |  | Νο.
D20 | Mains rehabilitation | Length of transmission and distribution mains rehabilitated the assessment period |  | km
D21 | Mains renovation | Length of mains renovated during the assessment period by epoxy resine, cement mortar or other materials |  | km
D22 | Mains replacement | Mains length replaced during the assessment period. |  | km
D23 | Replaced valves | Number of mains valves replaced during the assessment period. |  | Νο.
D24 | Service connection rehabilitation | Number of service connections replaced or renovated during the assessment period. |  | Νο.
D25 | Pumps overhaul | Total nominal power of pumps subject, during the assessment perid, to refurbishment of relevant elements, necessary to bring unit back to original performance. |  | kW
D26 | Pumpsreplacement | Total nominal power of pumps replaced during the assessment period. |  | kW
D27 | Pump failures | Sum, for all pumps, of the number of days during the assessment period when the pump is out of order. |  | days
D28 | Mains failures | Number of mains failures the assessment period, including failures of valves and fittings. |  | Νο.
D29 | Service connection failures | Number of service connection failures the assessment period. |  | Νο.
D30 | Hydrant failures | Number of hydrant failures during the assessment period. |  | Νο.
D31 | Power failures | Sum, for all water pumping stations, of the number of hours during the assessment peiod each pumping station is out of service due to power supply interruptions. |  | hours
D32 | Water-point failures | Number of water-points failures during the reference period. |  | Νο.
D33 | Delivery points with adequate pressure | Number of delivery points that receive and are likely to receive pressure equal to or above the guaranteed or declared terget level at the peak demand hour (but not when demand is abnornal), at the reference date. |  | Νο.
D34 | Average operating pressure | Average operating pressure at the delivery points when system is pressurised, at the reference date. |  | kPa
D35 | Water interruptions | Sum, for all water interruptions, of the population subject to a water interruption multiplied by the duration of the interruption in hours), during the assessment period. |  | persons*hours
D36 | Service interruptions | Total number of water interruptions, during the assessment period. |  | Νο.
D37 | Water use restrictions | Sum, for all the restrictions to water service occurred during the assessment period, of the population affected by each restriction to water service multiplied by the reprective duration in hours. |  | persons*hours
D38 | Days with restrictions to water service | Total number of days with restrictions to water service during the assessment period. |  | days
D39 | Residential customer meter reading frequency | Frequency of residential customer meter readings, pre-defined by the water undertaking for the assessment period. |  | Νο./meter/year
D40 | Industrial customer meter reading frequency | Frequency of industrial customer meter readings, pre-defined by the water undertaking for the assessment period. |  | Νο./meter/year
D41 | Bulk customer meter reading frequency | Frequency of bulk customer meter readings, pre-defined by the water undertaking for the assessment period. |  | Νο./meter/year
D42 | Customer meter readings | Total number of effective meter readings carried out during the assessment period for all types of metered customers. |  | Νο.
D43 | Residential customer meter readings | Total number of effective meter readings carried out during the assessment period for all types of residential customers. |  | Νο.
D44 | Opeational meters | Number of direct customer meters that are not out-of-service at the reference time. |  | Νο.
D45 | Meter replacement | Number of customer meters replaced in the system during the reference period. |  | Νο.
D46 | Required treated water quality tests carried out | Number of treated water tests carried out during the assessment period that are required by applicable standards or legislation. | 0 | Νο.
D47 | Required aesthetic tests carried out | Number of aesthetic tests of treated water tests carried out during the assessment period that are required by applicable standards or legislation. |  | Νο.
D48 | Required microbiological tests carried out | Number of microbiological tests of treated water tests carried out during the assessment period that are required by applicable standards or legislation. |  | Νο.
D49 | Required physical-chemical tests carried out | Number of physical-chemical tests of treated water tests carried out during the assessment period that are required by applicable standards or legislation. |  | Νο.
D50 | Required radioactivity tests carried out | Number of radioactivity tests of treated water tests carried out during the assessment period that are required by applicable standards or legislation. |  | Νο.
D51 | Treated water quality tests carried out | Number of treated water tests carried out during the assessment period. | 0 | Νο.
D52 | Water quality tests carried out | Total number of tests carried out by the water undertaking laboratories during the assessment period. |  | Νο.
D53 | Aesthetic tests carried out | Number of aesthetic tests of treated water carried out during the assessment period. |  | Νο.
D54 | Microbiological tests carried out | Number of microbiological tests of treated water carried out during the assessment period. |  | Νο.
D55 | Physical-chemical tests carried out | Number of physical-chemical tests of treated water carried out during the assessment period. |  | Νο.
D56 | Radioactivity tests carried out | Number of radioactivity tests of treated water tests carried out during the assessment period. |  | Νο.
D57 | Water quality tests required | Number of treated water tests required by applicable standards or legislation during the assessment period. | 0 | Νο.
D58 | Aesthetic tests required | Number of aesthetic tests of treated water required by applicable standards or legislation during the assessment period. |  | Νο.
D59 | Microbiological tests required | Number of microbiological tests of treated water required by applicable standards or legislation during the assessment period. |  | Νο.
D60 | Physical-chemical tests required | Number of physical-chemical tests of treated water required by applicable standards or legislation during the assessment period. |  | Νο.
D61 | Radioactivity tests required | Number of radioavtivity tests of treated water required by applicable standards or legislation during the assessment period. |  | Νο.
D62 | Compliance of aesthetic tests | Number of aesthetic tests of treated water carried out during the assessment period,which comply with the applicable standards or legislation. |  | Νο.
D63 | Compliance of microbiological tests | Number of microbiological of treated water carried out during the assessment period,which comply with the applicable standards or legislation. |  | Νο.
D64 | Compliance of physical-chemical tests | Number of physical-chemical of treated water carried out during the assessment period,which comply with the applicable standards or legislation. |  | Νο.
D65 | Compliance of radioactivity tests | Number of radioactivity of treated water carried out during the assessment period,which comply with the applicable standards or legislation. |  | Νο.
Ε1 | Households and businesses supplied | Total number of households and business connected to the water supply system at the reference time. |  | Νο.
Ε2 | Building supplies | Total number of buildings connected to the water supply system at the reference time. |  | Νο.
Ε3 | Households and businesses | Total number of households and business of the area of influence of the water undertaking regarding water supply, at the reference time. |  | Νο.
Ε4 | Buildings | Total number of buildings of the area of influence of the water undertaking regarding water supply, at the reference time. |  | Νο.
Ε5 | Resident population | Total population who lives on a permanent basis in the area served by the water undertaking, at the reference date. |  | persons
Ε6 | Direct customer meters | Total number of direct customer water meters at the reference date. |  | Νο.
Ε7 | Residential customer meters | Total number of residential customer water meters at the reference date. |  | Νο.
Ε8 | Industrial customer meters | Total number of industrial customer water meters at the reference date. |  | Νο.
Ε9 | Bulk customer meters | Total number of bulk customer water meters at the reference date. |  | Νο.
Ε10 | Registered customers | Total number of registered water supply customers at the reference date. |  | customers
Ε11 | Residential registered customers | Total number of residential registered water supply customers at the reference date. |  | customers
F1 | Population supplied | Resident population served by the water undertaking at the reference date. | 0 | persons
F2 | Population supplied with service pipes | Resident population served by the water undertaking through service connections at the reference date. |  | persons
F3 | Population served by public taps or standpipes | Resident population served by the water undertaking by public taps or standpipes at the reference date. |  | persons
F4 | Distance from water points to households | Sum, for all water points, of the distance between the water point and the far-most household served by it, at the reference date. |  | m
F5 | Public taps and standpipes consumption | Sum, for all public taps and standpipes,of the respective water consumption during the assessment period. |  | m3
F6 | Water points | Total number of water-points at the reference date. |  | Νο.
F7 | Operational water-points | Total number of water-points that are not out of service at the reference date. |  | Νο.
F8 | Public taps and standpipes | Total number of public taps and standpipes,at the assessment period. |  | Νο.
F9 | New connections establishment time | Sum, for all new connections established during the reference period, of the total time spent from the customer request until the availability of the water service. |  | days
F10 | New connections established | Total number of new connections established during the reference period. |  | Νο.
F11 | Customer meter installation time | Sum, for all new customer meters installed during the assessment period, of the total time spent from the customer request until the availability of the service. |  | days
F12 | New customer meters installed | Total number of new water customer meters installed during the assessment period. |  | Νο.
F13 | Connections repair time | Sum, for all service connections repaired during the assessment period, of the total time spent from the time failures are reported until the service is resumed. |  | days
F14 | Connections repaired | Total number of water connections repaired during the assessment period. |  | Νο.
F15 | Service complaints | Number of direct, telephone, and written complaints of quality of service during the assessment period. | 0 | Νο.
F16 | Pressure complaints | Number of pressure complaints during the assessment period. |  | Νο.
F17 | Continuity complaints | Number of continuity complaints regarding the water supply service during the assessment period. |  | Νο.
F18 | Water quality complaints | Number of water quality complaints during the assessment period. |  | Νο.
F19 | Complaints on interruptions | Number of complaints due to water supply interruptions during the assessment period. |  | Νο.
F20 | Billing complaints and queries | Number of direct, telephone, and written billings complaints and queries regarding the water supply service, during the assessment period. |  | Νο.
F21 | Other complaints and queries | Number of other complaints and queries regarding the water supply service, during the assessment period. |  | Νο.
F22 | Written responses | Number of written responses to written queries and complaints within the target time regarding the water supply service, during the assessment period. |  | Νο.
F23 | Written complaints | Number of written complaints regarding the water supply service, during the assessment period. |  | Νο.
G1 | Total revenues | Total operating revenues minus capitalised costs of self-constructed assets, regarding the water supply service, during the assessment period. | 0 | EUR
G2 | Operating revenues | Total operating revenues during the assessment period, including sales revenues (G3), work in progress, capitalised costs of self-constructed assets (G35) and other operating revenues, regarding the water supply service. |  | EUR
G3 | Sales revenues | Operating revenues from sales during the assessment, regarding the water supply service. |  | EUR
G4 | Total costs | Total costs during the assessment period, including capital and running costs, regarding the water supply service. | 0 | EUR
G5 | Running costs | Total operations and maintenance net costs and internal manpower net costs (i.e. not including the capitalised costs of self costructed assets) during the assessment period, regarding the water supply service. | 0 | EUR
G6 | Capital costs | Total net interest and depreciation (based on book values) during the assessment period, regarding the water supply service. | 0 | EUR
G7 | Operational costs | Operational costs during the assessment period regarding the water supply service, including the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of imported (raw and treated) water, energy, external services, leasing and rentals, chemicals, other consumables and materials for maintenance and repair, taxes, levies & fees and ecxeptional earning &losses, and other operating costs. Manpower shall not be included. | 0 | EUR
G8 | Internal manpower costs | Internal manpower costs during the assessment period regarding the water supply service, referred to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the personnel which salary is paid directly by the water undertaking. |  | EUR
G9 | External services costs | The net value (obtained by negative apportionment of related capitalised costs of self-costructed assets) of total costs of external services (i.e. outsourcing), external manpower costs included, regarding the water supply service, during the assessment period. |  | EUR
G10 | Imported (raw and treated) water costs | Total cost of the water imported (raw and treated) during the assessment period. |  | EUR
G11 | Electrical energy costs | Total costs of electrical energy (including energy of pumping and for other water supply undertaking activities such as workshops, office buildings energy consumption, laboratories, etc), withinthe period of assessment, regarding the water supply service. |  | EUR
G12 | Purchased merchandises | The net value (obtained by negative apportionment of related capitalised costs of self-costructed assets) of all materials, chemicals and other consumables not including in external services costs, regarding the water supply service, during the assessment period. |  | EUR
G13 | Leasing and rentals | The net value (obtained by negative apportionment of related capitalised costs of self-costructed assets) of total cost of leasing and rentals, regarding the water supply service, during the assessment period. |  | EUR
G14 | Taxes, levies and fees | All levies and licences strictly connected with the water supply system's operation to be paid to a govemmental or municipal authority (including direct taxes on EBT), during the assessment period. |  | EUR
G15 | Exceptional earnings and losses | Exceptional income or expenditures related to sales/writing-off of fixed assets, regarding the water supply service, during the assessment period. |  | EUR
G16 | Other oparating costs | The net value (obtained by negative apportionment of related capitalised costs of self-costructed assets) of other operating costs, not included in chemicals, other consumables and materials for maintance and repair, leasing and rentals, taxes, levies and fees and exceptional earnings & losses, regarding the water supply service, during the assessment period. |  | EUR
G17 | General management running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of costs of directorate, central administration, strategic planning, marketing and comunications, other stakeholder relations, legal affairs, internal audits, environmental management, new biseness development and general computing support activities, regarding the water supply service, during the assessment period. |  | EUR
G18 | Human resources management running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of costs of personnel administration, education and training, occupational safety, health services activities and social activities, regarding the water supply service, during the assessment period. |  | EUR
G19 | Financial and commercial running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of costs of economic and financial planning, economic administration, economic controlling and purchasing and material management activities, regarding the water supply service, during the assessment period. |  | EUR
G20 | Customer service running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of costs of meter reading, accounting and control, customer relations and management activities, regarding the water supply service, during the assessment period. |  | EUR
G21 | Planning, design, construction, operationa & maintenance running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the water supply technical planning, design, construction, operations and maintenance (including asset repair), during the assessment period. |  | EUR
G22 | Water resources and catchment management running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the water recources and catchment management, during the assessment period. |  | EUR
G23 | Abstraction and treatment running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the abstraction and treatment, during the assessment period. |  | EUR
G24 | Transmission, storage and distribution running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the transmission, storage and distribution, during the assessment period. |  | EUR
G25 | Water quality sampling and testing running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the water quality sampling and testing, during the assessment period. |  | EUR
G26 | Meter management running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the water meter management, during the assessment period. |  | EUR
G27 | Support services running costs | Part of the running cost related to the net value (obtained by negative apportionment of related capitalised costs of self-constructed assets) of the support services,regarding the water supply service, during the assessment period. |  | EUR
G28 | Depreciation costs | Depreciation costs (on book values), regarding the water supply service, during the assessment period. |  | EUR
G29 | Interest expenses costs | Interest expenses costs, regarding the water supply service, during the assessment period. |  | EUR
G30 | Interest income | Total interest income, regarding the water supply service, during the assessment period. |  | EUR
G31 | Net interest | Interest expenses costs, regarding the water supply service, during the assessment period. | 0 | EUR
G32 | Investment in tangible assets | Total cost of the investments in tangible (expenditures for plant and equipment), including capitalised cost of self-costructed tangible assets (the part of the G35 related to tangible assets), regarding the water supply service, during the assessment period. | 0 | EUR
G33 | Investments for new assets and reinforcement of existing assets | Total cost of the investments in tangible assets that constitute a new development for the service (new assets and reinforcement of existing assets), including capitalised cost of self-costructed tangible assets (part of the G35 related to tangible assets newly constructed or reinforced), regarding the water supply service, during the assessment period. |  | EUR
G34 | Investments for asset replacement and renovation | Total cost of the investments related to the replacement and renovation of existing water supply assets ("like for like", i.e., maintaining the approximately the same functionality of existing infrastructure), including capitalised cost of self-construction (part of G35 related to the replacement or renovaation of tangible assets), during the assessment period. |  | EUR
G35 | Capitalised cost of self-constructed assets | Total capitalised cost of self-constructed assets during the assessment period, regarding the water supply service. |  | EUR
G36 | Water sales revenue for direct consumption | Water sales revenue for direct water consumption during the assessment period. |  | EUR
G37 | Water sales revenue fro exported water | Water sales revenue for exported water. |  | EUR
G38 | Accounts receivable | Accounts receivable from drinking water, at the reference date. |  | EUR
G39 | Investments subject to depreciation | Investments for assets subject to depreciation according to the accounting principles generally accepted, regarding the water supply service, during the assessment period. |  | EUR
G40 | Investments financed by the cash flow | Investments financed by the cash flow (assessed as the sum of net income, depreciation and working capital variation), regarding the water supply service, during the assessment period. |  | EUR
G41 | Depreciated historical value of tangible assets | Sum, for all the tangible assets, of the depreciation value applied, since the date of purchase, regarding the water supply service. |  | EUR
G42 | Historical value of tangible assets | Refers to the gross book value of total expenditures at the reference date in infrastructure and non-infrastructure tangible assets, regarding the water supply service. |  | EUR
G43 | Annual debt from customers | Annual debt from customers, regarding the water supply service. | 0 | EUR
G44 | Annual amount billed per year | Annual amount billed during the year, regarding the water supply service. |  | EUR
G45 | Cash flow | Total available is the sum of net income, depreciaton and the net value of decrease or increase in working capital, regarding the water supply servicem during the assessment period. |  | EUR
G46 | Financial debt service | The financial debt service contains the expenditures for interest (G29), the cost of loans, and the principal (=capital) repayment debt instruments, regarding the water supply service, during the assessment period. |  | EUR
G47 | Total debt | Sum of long term liabilities (bonds and long term financial debts) and current liabilities, at the end of the fiscal year, regarding the water supply service. | 0 | EUR
G48 | Shareholders' equity | Surplus of the asset over the liabilities, at the end of the fiscal year, regarding the water supply service | 0 | EUR
G49 | Current assets | Current assets include cash at bank and in hand, accounts receivable from drinking water, other accounts receivable, inventories and prepaid expenses, at the reference date, regarding the water supply service. |  | EUR
G50 | Total assets | Sum of the intangible assets (including goodwill and net value of licences and rights), tangible assets (including net value of water undertaking plants and net value of other assets), financial assets (including net net value of financial investments) and current assets (G49), regarding the water supply service, at the end of the fiscal year. |  | EUR
G51 | Inventories | Accounted value of materials to be used in the production, process that are in stock in the undertaking at the reference date, regarding the water supply service |  | EUR
G52 | Long term liabilities | Sum of bonds and long term financialdebts at the reference date, regarding the water supply service. |  | EUR
G53 | Current liabilities | Current liabilities include accounts payable, current portion of long term debt and miscellaneous current liabilities, at the reference date, regarding the water supply service. |  | EUR
G54 | Operating income | Earning before interest and taxes (EBIT), regarding the water supply service, during the year. |  | EUR
G55 | Operating income related taxes | Subset of the total taxes specifically related to the operating income (EBIT), regarding the water supply service, during the year. |  | EUR
G56 | Net income | Net income after interest payment and taxes, regarding the water supply service, at the end of the fiscal year. |  | EUR
G57 | Average water charges for direct consumption | Ratio bewteen the water sales revenue for direct consumption and billed water. | #DIV/0! | EUR/m3
G58 | Attributed unit cost for real losses | Highest of the variable component of improved water charge or long run marginal cost (LRMC) for own sources. |  | EUR/m3
H1 | Assessment period | Period of time adopted for the assessment of the data and the PI. |  | days
H2 | Time system is pressurised | Amount of time of the year the system in pressurised. |  | hours

## PIs
Α/Α | GROUP | PERFORMANCE INDICATORS | MEANING | FORMULA | VALUE | MEASURED IN | COMMENTS
WR1 | Water Resources | Inefficiency of use or water resources | (Real losses during the assessment period / system input volume during the assessment period) x 100 | WR1=(A19/A3)*100 | #DIV/0! | %
WR2 |  | Water resources availability | (System input volume during the assessment period x 365 / assessment period) / (annual yield capacity of own recourses + annual imported water allowance) x 100 | WR2=((A3*365/H1)/(A1+A2))*100 | #DIV/0! | %
WR3 |  | Own water resources availability | ((System input volume during the assessment period x 365 / assessment period)/ annual yield capacity of own recourses)) x 100 | WR3=((A3*365/H1)/A1)*100 | #DIV/0! | %
WR4 |  | Reused supplied water | Reused supplied water during the assessment period / system input volume during the assessment period x 100 | WR4=(A22/A3)*100 | #DIV/0! | %
Pe1 | Total Personnel | Employees per connection | Number of full time equivalent employees of the water undertaking / number of service connections x 1000 | Pe1=(B1/C24)*1000 | #DIV/0! | Νο./1000 connections
Pe2 |  | Employees per water produced | (Number of full time equivalent employees of the water undertaking / (water produced the assessment period x 365 / assessment period)) x 10^6 | Pe2=[B1/(A6*365/H1)]*10^6 | #DIV/0! | Νο./(10^6m3/year)
Pe3 | Personnel per main function | General management personnel | Number of full time equivalent employees dedicated to directorate, central administration, strategic planning, marketing and comunications, other stakeholder relations, legal affairs, internal audits, environmental management, new business development and general co. | Pe3=(B2/B1)*100 | #DIV/0! | %
Pe4 |  | Human resources management personnel | (Number of full time equivalent employees dedicated to personnel administration, education and training, occupational safety and health services and social activities / Number of full time equivalent employees of the water undertaking) x 100 | Pe4=(B3/B1)*100 | #DIV/0! | %
Pe5 |  | Financial and commercial personnel | (Number of full time equivalent employees dedicated to economic and financial planning, economic administration, economic controlling and purchasing and material management / Number of full time equivalent employees of the water undertaking) x 100 | Pe5=(B4/B1)*100 | #DIV/0! | %
Pe6 |  | Customer service personnel | (Number of full time equivalent employees dedicated to accounting and control and to customer relations and management activities / Number of full time equivalent employees of the water undertaking) x 100 | Pe6=(B5/B1)*100 | #DIV/0! | %
Pe7 |  | Technical services personnel | (Number of full time equivalent employees dedicated to planning, construction, operations and maintenance activities / Number of full time equivalent employees of the water undertaking) x 100 | Pe7=(B6/B1)*100 | #DIV/0! | %
Pe8 |  | Planning and construction personnel | (Number of full time equivalent employees of technical services working in planning & construction / Number of full time equivalent employees of the water undertaking) x 100 | Pe8=(B7/B1)*100 | #DIV/0! | %
Pe9 |  | Operations and maintenance personnel | (Number of full time equivalent employees of technical services working in operations & maintenance / Number of full time equivalent employees of the water undertaking) x 100 | Pe9=(B8/B1)*100 | #DIV/0! | %
Pe10 | Technical services personnel per activity | Water resources and catchment management personnel | [Number of full time equivalent employees working in the water resources and catchment management / (water produced during the assessment period x 365)/assessment period)]*10^6 | Pe10=[B9/(A6*365/H1)]*10^6 | #DIV/0! | Νο./(10^6m3/year)
Pe11 |  | Abstraction and treatment personnel | [Number of full time equivalent employees working in planning, design, construction, operations and maintenance of the abstraction and treatment / (water produced during the assessment period x 365)/assessment period)]*10^6 | Pe11=[B10/(A6*365/H1)]*10^6 | #DIV/0! | Νο./(10^6m3/year)
Pe12 |  | Transmission, storage and distribution personnel | (Number of full time equivalent employees working in planning, design, construction, operations and maintenance of the transmission, storage and distribution system / total mains length) x 100 | Pe12=(B11/C8)*100 | #DIV/0! | Νο./100 km
Pe13 |  | Water quality monitoring personnel | [Number of full time equivalent employees working in water quality sampling and testing / (total number of tests carried out by the undertaking laboratories during the assessment period x 365 / assessment period)]*10000 | Pe13=[B12/(D52*365/H1)]*10000 | #DIV/0! | Νο./10000 tests/year
Pe14 |  | Meter management personnel | (Number of full time equivalent employees working in meter management / total number of system and customer meters) x 10000 | Pe14=[B13/(C10+E6)]*1000 | #DIV/0! | Νο./1000 meters
Pe15 |  | Support services personnel | (Number of full time equivalent employees working in support services / total number of full time equivalent employees working in technical services) x 100 | Pe15=(B14/B6)*100 | #DIV/0! | %
Pe16 | Personnel qualification | University degree personnel | (Number of full time equivalent employees of the water undertaking with university degree / number of full time equivalent employees of the water undertaking) x 100 | Pe16=(B15/B1)*100 | #DIV/0! | %
Pe17 |  | Basic education personnel | (Number of full time equivalent employees of the water undertaking with basic education / number of full time equivalent employees of the water undertaking) x 100 | Pe17=(B16/B1)*100 | #DIV/0! | %
Pe18 |  | Other qualification personnel | (Number of full time equivalent employees of the water undertaking with basic education / number of full time equivalent employees of the water undertaking) x 100 | Pe18=(B17/B1)*100 | #DIV/0! | %
Pe19 | Personnel training | Total training | [(Number of training hours during the assessment period x 365)/assessment period]/number of full time equivalent employees of the water undertaking | Pe19=[(B18*365)/H1]/B1 | #DIV/0! | hours / employee / year
Pe20 |  | Internal training | Number of internal training hours / number of full time equivalent of the water undertaking | Pe20=[(B19*365)/H1]/B1 | #DIV/0! | hours / employee / year
Pe21 |  | External training | [(Number of external training hours during the assessment period x 365)/assessment period]/number of full time equivalent employees of the water undertaking | Pe21=[(B20*365)/H1]/B1 | #DIV/0! | hours / employee / year
Pe22 | Personnel health and safety | Working accidents | {[(Number of working accidents requiring medical care occuring with personnel during the assessment period x 365)/assessment period]/number of full time equivalent employees of the water undertaking} x 100 | Pe22={[(B21*365)/H1]/B1}*100 | #DIV/0! | Νο./100 employees/year
Pe23 |  | Absebteeism | [(Total number of days of absenteeism occuring during the assessment period x 365)/assessment period]/number of full time equivalent employees of the water undertaking | Pe23=[(B22*365)/H1]/B1 | #DIV/0! | days / employee / year
Pe24 |  | Absedeeism due to working accidents or illness at work | [(Total number of days of absenteeism due to accindets or illness at work occuring during the assessment period x 365)/assessment period]/number of full time equivalent employees of the water undertaking | Pe24=[(B23*365)/H1]/B1 | #DIV/0! | days / employee / year
Pe25 |  | Absedeeism due to other reasons | [(Total number of days of absenteeism occuring during the assessment period that were not due to working accidents or illness at work x 365)/assessment period]/number of full time equivalent employees of the water undertaking | Pe25=[(B24*365)/H1]/B1 | #DIV/0! | days / employee / year
Pe26 | Overtime work | Overtime work | (Overtime work during the assessment period / normal work during the assessment period) x 100 | Pe26=(B26/B25)*100 | #DIV/0! | %
Ph1 | Treatment | Treatment plant utilisation | (Maximum daily volume of water treated in treatment plants during the assessment period / maximum daily capacity of the existing treatment plants) x 100 | Ph1=(A4/C3)*100 | #DIV/0! | %
Ph2 | Storage | Raw water storage capacity | (Net capacity of raw water reservoirs / system input volume during the assessment period) x assessment period | Ph2=(C1/A3)*H1 | #DIV/0! | days
Ph3 |  | Transmission and distribution storage capacity | (Total capacity of treated water reservoirs (private storage tanks excluded)/ system input volume during the assessment period) x assessment period | Ph3=(C2/A3)*H1 | #DIV/0! | days
Ph4 | Pumping | Pumping utilisation | [Sum, for all installed pumps, of the number of operation hours of the maximum energy consumption day during the assessment period multiplied by the nominal power of the pump / (maximum nominal power that can be used simultaneously in the system x 24)] x 100 | Ph4=[D2/(C7*24)]*100 | #DIV/0! | %
Ph5 |  | Standardised energy consumption | Energy consumption for pumping during the assessment period / Sum of the volume elevated during the assessment period multiplied by the pump head / 100 | Ph5=D1/D3 | #DIV/0! | kWh/m3/100m
Ph6 | Treatment | Reactive energy consumption | Reactive energy consumption for pumping during the assessment period / total energy consumption for the pumping during the assessment period multiplied by the pump head x 100 | Ph6=(D4/D1)*100 | #DIV/0! | %
Ph7 |  | Energy recovery | (Enenrgy recoverd by the use of turbines of reverse pumps during the assessment period / total energy consumption for pumping during the assessment priod) x 100 | Ph7=(D5/D1)*100 | #DIV/0! | %
Ph8 | Transmission and distribution | Valve density | Number of isolating valves / total distribution mains length | Ph8=C22/C9 | #DIV/0! | No./km
Ph9 |  | Hydrant density | Number of hydrants / total distribution mains length | Ph9=C23/C9 | #DIV/0! | No./km
Ph10 | Meters | District meter density | (Number of district meters / number of service connections) x 100 | Ph10=(C11/C24)*1000 | #DIV/0! | No./1000 service connections
Ph11 |  | Customer meter density | Number of direct customer meters / number of service connections | Ph11=E6/C24 | #DIV/0! | Νο./service connections
Ph12 |  | Metered customers | Number of direct and bulk customer meters / number of registered customers | Ph12=(E6+E9)/E10 | #DIV/0! | Νο./ customer
Ph13 |  | Metered residential customers | Number of residential-equivalent customer meters / number of residential registered customers | Ph13=E7/E11 | #DIV/0! | Νο./ customer
Ph14 | Automation and control | Automation degree | (Number of automated control units / number of control units) x 100 | Ph14=(C16/C15)*100 | #DIV/0! | %
Ph15 |  | Remote control degree | (Number of remotely controlled units / number of control units) x 100 | Ph15=(C17/C15)*100 | #DIV/0! | %
Op1 | Inspection and maintenance of physical assets | Pump inspection | [(Total nominal power of pumps and related ancillaries subjected to inspection during the assessment period x 365) / assessment period] / total nominal power of pumps | Op1=[(D6*365)/H1]/C6 | #DIV/0! | / year
Op2 |  | Storage tank cleaning | [(Volume of storage tank cells sleaned during the assessment period x 365) / assessment period] / total volume of storage tank cells | Op2=[(D7*365)/H1]/C2 | #DIV/0! | / year
Op3 |  | Network inspection | [(Length of transmission and distribution mains where at least valves and other fittings were inspected duting the assessment period x 365) / assessment period) / total mains legth] x 100 | Op3=[(D8*365)/H1/C8]*100 | #DIV/0! | % / year
Op4 |  | Leakage control | [(Length of mains subject to active leakage control during the assessment period x 365) / assessment period) / total mains legth] x 100 | Op4=[(D9*365)/H1/C8]*100 | #DIV/0! | % / year
Op5 |  | Active leakage control repairs | [(Number of leaks detected and repaired due to active leakage control during the assessment period x 365) / assessment period) / total mains legth] x 100 | Op5=[(D10*365)/H1/C8]*100 | #DIV/0! | Νο./100km/year
Op6 |  | Hydrant inspection | [(Number of hydrants inspected during the assessment period x 365) / assessment period) / total number of hydrants] x 100 | Op6=[(D11*365)/H1]/C23 | #DIV/0! | / year
Op7 | Instrumentation calibration | System flow meters calibration | [(Number of system flowmeter calibrations carried out during the assessment period x 365) / assessment period)] / number of system flow meters intsalled in the system (permanently or temporarily) | Op7=[(D12*365)/H1]/C10 | #DIV/0! | / year
Op8 |  | Meter replacement | [(Number of customer flow meters replaced during the assessment period x 365) / assessment period)] / number of customer meters | Op8=[(D45*365)/H1]/Ε6 | #DIV/0! | / year
Op9 |  | Pressure meters calibration | [(Number of pressure meter calibrations carried out during the assessment period x 365) / assessment period)] / number of pressure meters intsalled in the system (permanently or temporarily) | Op9=[(D13*365)/H1]/C12 | #DIV/0! | / year
Op10 |  | Water level meters calibration | [(Number of water level meter calibrations carried out during the assessment period x 365) / assessment period)] / number of water level meters intsalled in the system (permanently or temporarily) | Op10=(D14*365/H1)/C13 | #DIV/0! | / year
Op11 |  | On-line water quality monitoring equipment calibration | [(Number of on-line water quality monitoring instrument calibrations carried out during the assessment period x 365) / assessment period)] / number of on-line water quality instrument intsalled in the system (permanently or temporarily) | Op11=[(D15*365)/H1]/C14 | #DIV/0! | / year
Op12 | Electrical & signal transmission equipment inspection | Emergency power system inspection | [(Sum of the nominal power of the emergency power systems inspected during the assessment period x 365) / assessment period)] / total nominal power of the emergency power systems | Op12=[(D16*365)/H1]/C18 | #DIV/0! | / year
Op13 |  | Signal transmission equipment inspection | [(Number of the signal transmission units inspected during the assessment period x 365) / assessment period)] / total number of signal transmission units | Op13=[(D17*365)/H1]/C19 | #DIV/0! | / year
Op14 |  | Electrical switchgear equipment inspection | [(Number of electrical switchgear units inspected during the assessment period x 365) / assessment period)] / total number of electrical switchgear units | Op14=[(D18*365)/H1]/C20 | #DIV/0! | / year
Op15 | Vehicle availability | Vehicle availability | Number of vehicles daily available, on a permanent basis, in average, for field works in operations and maintenance activities / total mains length x 100 | Op15=(D19/C8)*100 | #DIV/0! | Νο./100km
Op16 | Mains, valves and service connection rehabilitation | Mains rehabilitation | [(Length of transmission and distribution mains rehabilitated during the assessment period x 365) / assessment period)] / total mains length] x 100 | Op16=[(D20*365)/H1/C8]*100 | #DIV/0! | % / year
Op17 |  | Mains renovation | [(Length of transmission and distribution mains rehabilitated during the assessment period x 365) / assessment period)] / total mains length] x 100 | Op17=[(D21*365)/H1/C8]*100 | #DIV/0! | % / year
Op18 |  | Mains replacement | [(Length of mains replaced during the assessment period x 365) / assessment period)] / total mains length] x 100 | Op18=[(D22*365)/H1/C8]*100 | #DIV/0! | % / year
Op19 | Inspection & maintenance of physical assets | Replaced valves | [(Number of mains valves replaced during the assessment period x 365) / assessment period)] / total number of mains valves] x 100 | Op19=[(D23*365)/H1/C21]*100 | #DIV/0! | % / year
Op20 |  | Service connection rehabilitation | [(Number of service connections replaced or renovated during the assessment period x 365) / assessment period)] / total number of service connections] x 100 | Op20=[(D24*365)/H1/C24]*100 | #DIV/0! | % / year
Op21 | Pumps rehabilitation | Pump refurbishment | [(Total nominal power of pumps subject to overhaul during the assessment period x 365) / assessment period)] / total nominal power of pumps] x 100 | Op21=[(D25*365)/H1/C6]*100 | #DIV/0! | % / year
Op22 |  | Pump replacement | [(Total nominal power of pumps replaced during the assessment period x 365) / assessment period)] / total nominal power of pumps] x 100 | Op22=[(D26*365)/H1/C6]*100 | #DIV/0! | % / year
Op23 | Operational Water Losses | Water losses per connection | [(Water losses during the assessmnent period x 365) / assessment period]/number of service connections | Op23=[(Α15*365)/H1]/C24 | #DIV/0! | m3/ connection / year
Op24 |  | Water losses per mains length | (Water losses during the assessmnent period / assessment period)/mains length | Op24=(A15/H1)/C8 | #DIV/0! | m3/km/year
Op25 |  | Apparent losses | [Apparent losses / (system input volume - exported water )] x 100 | Op25=[A18/(A3-A5-A7)]*100 | #DIV/0! | %
Op26 |  | Apparent losses per system input volume | Apparent losses during the assessment period / system input volume x 100 | Op26=(A18/A3)*100 | #DIV/0! | %
Op27 |  | Real losses per connection | (Real losses during the assessment period x 1000) / [(number of service connections x number of hours system is pressurised during the assessment period)/24] | Op27=(Α19*1000)/[(C24*Η2)/24] | #DIV/0! | lt/connection/day when system is pressurised
Op28 |  | Real losses per mains length | (Real losses during the assessment period x 1000) / [(mains length x number of hours system is pressurised during the assessment period)/24] | Op28=(Α19*1000)/[(C8*Η2)/24] | #DIV/0! | lt/km/day when system is pressurised
Op29 |  | Infrastructure Leakage Index (ILI) | Real losses (Op27) / technical achievable low-level real losses (when system is pressurised) | Op29=Op27/(18*C8/C24+0,8+0,025*C25)/(D34/10) | #DIV/0!
Op30 | Failure | Pump failures | [(Sum, for all pumps, of the number of days during the assessment period when the pump is out of order x 365) / assessment period] / total number of pumps | Op30=[(D27*365)/H1]/C4 | #DIV/0! | days / pump / year
Op31 |  | Mains failures | [(Number of mains failures during the assessment period (including failures of valves and fittings) x 365) / assessment period] / total mains length] x 100 | Op31=[(D28*365)/H1/C8]*100 | #DIV/0! | Νο./km/year
Op32 |  | Service connection failures | [(Number of service connection failures during the assessment period x 365) / assessment period] / number of service connections] x 1000 | Op32=[(D29*365)/H1/C24]*1000 | #DIV/0! | Νο./1000 connections / year
Op33 |  | Hydrant failures | [(Number of hydrant failures during the assessment period x 365) / assessment period] / number of hydrants] x 1000 | Op33=[(D30*365)/H1/C23]*1000 | #DIV/0! | Νο./1000 hydrants/ year
Op34 |  | Power failures | [(Sum, for all pumps, of the number of hours each pumping station is out of service due to power supply interruption during the assessment period x 365) / assessment period] / total number of pumping stations | Op34=[(D31*365)/H1]/C5 | #DIV/0! | hours / pumping station / year
Op35 |  | Water-point failures | Number of water-points failures during the reference period / total number of waterpoints | Op35=[(D32*365)/H1]/F6 | #DIV/0! | No./water point/year
Op36 | Water metering | Customer reading efficiency | [(Number of effective meter readings effective meter readings carried out during the assessment period x 365) / assessment period]/(number of residential customer meters x residential customer meter reading frequency + number of industrial customer meters x industrial customer meter reading frequency + number of bulk customer meters x bulk customer meter reading frequency) | Op36=[(D42*365)/H1]/(E7*D39+E8*D40+E9*D41) | #DIV/0!
Op37 |  | Residential customer reading efficiency | [(Number of effective residential meter reading carried out during the assessment period x 365)/assessment period]/(number of residential customer meters x residential customer meter reading frequency) | Op37=[(D43*365)/H1]/(Ε7*D39) | #DIV/0!
Op38 |  | Operational meters | (Number of direct customer meters installed that are not out-of-service at the reference time / number of direct meters) x 100 | Op38=(D44/E6)*100 | #DIV/0! | %
Op39 |  | Unmetered water | (System input volume-metered consumption / system input volume during the assessment period) x 100 | Op39=[(A3-A8-A11)/A3]*100 | #DIV/0! | %
Op40 | Water quality monitoring | Tests carried out | (Number of treated water carried out during the assessment period / number of reated water tests required by applicable standards or legislation during the assessment period) x 100 | Op40=(D46/D57)*100 | #DIV/0! | %
Op41 |  | Aesthetic tests carried out | (Number of aesthetic tests of treated water carried out during the assessment period / number of aesthetic tests of treated water required by applicable standards or legislation during the assessment period) x 100 | Op41=(D47/D58)*100 | #DIV/0! | %
Op42 |  | Microbiological tests carried out | (Number of microbiological tests of treated water carried out during the assessment period / number of microbiological tests of treated water required by applicable standards or legislation during the assessment period) x 100 | Op42=(D48/D59)*100 | #DIV/0! | %
Op43 |  | Physical-chemical tests carried out | (Number of physical-chemical tests of treated water carried out during the assessment period / number of physical-chemical tests of treated water required by applicable standards or legislation during the assessment period) x 100 | Op43=(D49/D60)*100 | #DIV/0! | %
Op44 |  | Radioactivity tests carried out | (Number of radioactivity tests of treated water carried out during the assessment period / number of radioactivity tests of treated water required by applicable standards or legislation during the assessment period) x 100 | Op44=(D50/D61)*100 | #DIV/0! | %
QS1 | Service coverage | Households and businesses supply coverage | (Number of households and businesses connected to the public network / total number of households and businesses) x 100 | QS1=(E1/E3)*100 | #DIV/0! | %
QS2 |  | Buildings supply coverage | (Number of buildings connected to the public network / total number of buildings and businesses) x 100 | QS2=(E2/E4)*100 | #DIV/0! | %
QS3 |  | Population coverage | (Resident population served by the water undertaking / total resident population) x 100 | QS3=(F1/E5)*100 | #DIV/0! | %
QS4 |  | Population coverage with service connections | (Resident population served by the water undertaking through service connections / total resident population) x 100 | QS4=(F2/E5)*100 | #DIV/0! | %
QS5 |  | Population coverage with public taps or standpipes | (Resident population served by the water undertaking through public taps or standpipes / total resident population) x 100 | QS5=(F3/E5)*100 | #DIV/0! | %
QS6 | Public taps and standpipes | Operational water points | (Number of water points that arenot out-of-service / number of water points) x 100 | QS6=(F7/F6)*100 | #DIV/0! | %
QS7 |  | Average distance from waterpoints to households | Sum, for all water points, of the distance between the water point and the far-most household served by it / total number of water points | QS7=F4/F6 | #DIV/0! | m
QS8 |  | Per capits water consumed in public taps and standpipes | (Sum, for all water points, of the water consumption at the water point during the assessment period x 1000 / resident population served by the water undertaking through public taps or standpipes) / assessment period | QS8=(F5*1000/F3)/H1 | #DIV/0! | lt/person/day
QS9 |  | Population per public tap or standpipe | Resident population served by the water undertaking through public taps or standpipes / number of public taps or standpipes | QS9=F3/F8 | #DIV/0! | persons/tap
QS10 | Pressure and continuity of supply | Pressure of supply adequacy | (Number of delivery points that receive and are likely to receive pressure equal to or above the guaranteed or declared target level at the peak demand hour (but not when demand is abnormal) / number of service connections) x 100 | QS10=(D33/C24)*100 | #DIV/0! | %
QS11 |  | Bulk supply adequacy | (Number of delivery points that are supplied at any time according to the target flow, volume and/ or pressure/number of delivery points) x 100 | QS11=(D33/E9)*100 | #DIV/0! | %
QS12 |  | Continuity of supply | [(Number of hours when the system is pressured during the assessment period/24)/assessment period)] x 100 | QS12=[(Η2/24)/Η1]*100 | #DIV/0! | %
QS13 |  | Water interruptions | [Sum, for the assessment period, of the population subject to a water multiplied by the respective duration of the interruption in hours / (population served x 24 x assessment period)] x 100 | QS13=[D35/(F1*24*H1)]*100 | #DIV/0! | %
QS14 |  | Interruptions per connection | {[(Total number of interruptions during the assessment period x 365)/assessment period]/number of service connections} x 1000 | QS14={[(D36*365)/H1]/C24}*1000 | #DIV/0! | No./1000 connections/year
QS15 |  | Bulk supply interruptions | [(Total number of interruptions during the assessment period x 365)/assessment period]/number of delivery points | QS15=[(D36*365)/H1)/E9 | #DIV/0! | No./delivery point/year
QS16 |  | Population experiencing restrictions to water service | [Sum, for the assessment period, of the population affected by restrictions to water service multiplied by the respective duration of therestrictions to water service in hours / (population served x 24 x assessment period)] x 100 | QS16=[D37/(F1*24*H1)]*100 | #DIV/0! | %
QS17 |  | Days with restrictions to water service | (Total number of days with restrictions to water service during the assessment period/assessment period) x 100 | QS17=(D38/H1)*100 | #DIV/0! | %
QS18 | Quality of supplied water | Quality of supplied water | [(Total number of treated water tests complying with the applicable standards or legislation during the assessment period/total number of tests of treated water carried out during the assessment period] x 100 | QS18=[(D62+D63+D64+D65)/D51]*100 | #DIV/0! | %
QS19 |  | Aesthetic tests compliance | (Number of aesthetic tests of treated water complying with the applicable standards or legislation during the assessment period/total number of aesthetic tests of treated water carried out during the assessment period) x 100 | QS19=(D62/D53)*100 | #DIV/0! | %
QS20 |  | Microbiological tests compliance | (Number of microbiological tests of treated water complying with the applicable standards or legislation during the assessment period/total number of microbiological tests of treated water carried out during the assessment period) x 100 | QS20=(D63/D54)*100 | #DIV/0! | %
QS21 |  | Physical-chemical tests compliance | (Number of physical-chemical tests of treated water complying with the applicable standards or legislation during the assessment period/total number of physical-chemical tests of treated water carried out during the assessment period) x 100 | QS21=(D64/D55)*100 | #DIV/0! | %
QS22 |  | Radioactivity tests compliance | (Number of radioactivity tests of treated water complying with the applicable standards or legislation during the assessment period/total number of radioactivity tests of treated water carried out during the assessment period) x 100 | QS22=(D65/D56)*100 | #DIV/0! | %
QS23 | Service connection and meter installation and repair | New connection efficiency | Total time spent for establishing new connections during the assessment period / number of new connections installed during the assessment period | QS23=F9/F10 | #DIV/0! | days
QS24 |  | Time to install a customer meter | Total time spent for customer meters during the assessment period / number of customer meters installed during the assessment period | QS24=F11/F12 | #DIV/0! | days
QS25 |  | Connection repair time | Total time spent for repairing service connections during the assessment period / total number of connections repaired during the assessment period | QS25=F13/F14 | #DIV/0! | days
QS26 | Customer complaints | Service complaints per connection | [(Number of complaints of quality of service during the assessment period x 365)/assessment period/number of service connections] x 1000 | QS26=[(F15*365)/H1/C24]*1000 | #DIV/0! | No.complaints/1000 connections/year
QS27 |  | Service complaints per customer | [(Number of complaints of quality of service during the assessment period x 365) /assessment period] /number of bulk supply customers | QS27=[(F15*365)/H1]/E10 | #DIV/0! | No.complaints/customer/year
QS28 |  | Pressure complaints | (Number of pressure complaints during the assessment period / number of service complaints during the assessment period) x 100 | QS28=(F16/F15)*100 | #DIV/0! | %
QS29 |  | Continuity complaints | (Number of continuity complaints during the assessment period / number of service complaints during the assessment period) x 100 | QS29=(F17/F15)*100 | #DIV/0! | %
QS30 |  | Water quality complaints | (Number of water quality complaints during the assessment period / number of service complaints during the assessment period) x 100 | QS30=(F18/F15)*100 | #DIV/0! | %
QS31 |  | Interruption complaints | (Number of complaints due to supply interruptions during the assessment period / number of service complaints during the assessment period) x 100 | QS31=(F19/F15)*100 | #DIV/0! | %
QS32 |  | Billing complaints and queries | [(Number of billing complaints and queries during the assessment period x 365)/ assessment period] / number of registered customers | QS32=[(F20*365)/H1]/E10 | #DIV/0! | Νο./customer/year
QS33 |  | Other complaints and queries | [(Number of other complaints and queries during the assessment period x 365)/ assessment period] / number of registered customers | QS33=[(F21*365)/H1]/E10 | #DIV/0! | Νο./customer/year
QS34 |  | Response to written complaints | (Number of written responses within the target time during the assessment period /number of written complaints during the assessment period) x 100 | QS34=(F22/F23)*100 | #DIV/0! | %
Fi1 | Revenues | Unit revenue | (Operating revenues - capitalised costs of self constructed assets) / authorised consumption (including exported water), during the assessment period | Fi1=(G2-G35)/A14 | #DIV/0! | EUR/m3
Fi2 |  | Sales revenues | (Self revenues / total revenues) x 100, during the assessment period | Fi2=(G3/G1)*100 | #DIV/0! | %
Fi3 |  | Other revenues | (Other revenues not coming from sales / total revenues) x 100, during the assessment period | Fi3=[(G1-G3)/G1]*100 | #DIV/0! | %
Fi4 | Costs | Unit total costs | (Running costs + capital costs) / autorised consumption (including exported water), during the assessment period | Fi4=G4/A14 | #DIV/0! | EUR/m3
Fi5 |  | Unit running costs | Running costs / autorised consumption (including exported water), during the assessment period | Fi5=G5/A14 | #DIV/0! | EUR/m3
Fi6 |  | Unit capital costs | Capital costs / authorised consumption (including exported water), during the assessment period | Fi6=G6/A14 | #DIV/0! | EUR/m3
Fi7 | Composition of running costs per type of costs | Internal manpower costs | (Internal manpower costs / running costs) x 100, during the assessment period | Fi7=(G8/G5)*100 | #DIV/0! | %
Fi8 |  | External services costs | (External services costs / running costs) x 100, during the assessment period | Fi8=(G9/G5)*100 | #DIV/0! | %
Fi9 |  | Imported (raw and treated) water costs | (Imported (raw and treated) water costs / running costs, during the assessment period) x 100 | Fi9=(G10/G5)*100 | #DIV/0! | %
Fi10 |  | Electrical energy costs | (Electrical energy costs / running costs) x 100, during the assessment period | Fi10=(G11/G5)*100 | #DIV/0! | %
Fi11 |  | Other costs | [(Purchased merchandises + leasing and rentals + taxes, levies & fees + exceptional earning & losses + other operating costs) / running costs] x 100 | Fi11=[(G12+G13+G14+G15+G16)/G5]*100 | #DIV/0! | %
Fi12 | Composition of running costs per main function of the water undertaking | General management functions costs | (Running costs of general management functions / running costs) x 100, during the assessment period | Fi12=(G17/G5)*100 | #DIV/0! | %
Fi13 |  | Human resources management functions costs | (Running costs of human resources management functions / running costs) x 100, during the assessment period | Fi13=(G18/G5)*100 | #DIV/0! | %
Fi14 |  | Financial and commercial functions costs | (Running costs of financial and commercial functions / running costs) x 100, during the assessment period | Fi14=(G19/G5)*100 | #DIV/0! | %
Fi15 |  | Customer service functions costs | (Running costs of customer service functions / running costs) x 100, during the assessment period | Fi15=(G20/G5)*100 | #DIV/0! | %
Fi16 |  | Technical services functions costs | (Running costs of the technical functions: planning, design, construction, operations and maintenance / running costs) x 100, during the assessment period | Fi16=(G21/G5)*100 | #DIV/0! | %
Fi17 | Composition of running costs per technical function activity | Water resources and catchment management costs | (Running costs of the water resources and catchment management / running costs) x 100, during the assessment period | Fi17=(G22/G5)*100 | #DIV/0! | %
Fi18 |  | Abstraction and treatment costs | (Running costs of the abstraction and treatment / running costs) x 100, during the assessment period | Fi18=(G23/G5)*100 | #DIV/0! | %
Fi19 |  | Transmission, storage and distribution costs | (Running costs of the transmission, storage and distribution / running costs) x 100, during the assessment period | Fi19=(G24/G5)*100 | #DIV/0! | %
Fi20 |  | Water quality monitoring costs | (Running costs of the water quality sampling and testing / running costs) x 100, during the assessment period | Fi20=(G25/G5)*100 | #DIV/0! | %
Fi21 |  | Meter management costs | (Running costs of the meter management / running costs) x 100, during the assessment period | Fi21=(G26/G5)*100 | #DIV/0! | %
Fi22 |  | Support services costs | (Running costs of the support services / running costs) x 100, during the assessment period | Fi22=(G27/G5)*100 | #DIV/0! | %
Fi23 | Composition of capital costs | Depreciation costs | (Depreciation costs / capital costs) x 100, during the assessment period | Fi23=(G28/G6)*100 | #DIV/0! | %
Fi24 |  | Net interest costs | (Interest expenses costs - interest income / capital costs) x 100, during the assessment period | Fi24=[(G29-G30)/G6]*100 | #DIV/0! | %
Fi25 | Investment | Unit investment | Cost of investements (expenditures for plant and equipment) / autorised consumption (including exported water), during the assessment period | Fi25=G32/A14 | #DIV/0! | EUR/m3
Fi26 |  | Investments for new assets and reinforcement of existing assets | (Cost of investements for new assets and reinforcement of existing assets / total cost of the investement) x 100, during the assessment period | Fi26=(G33/G32)*100 | #DIV/0! | %
Fi27 |  | Investments for asset replacement and renovation | (Cost of investements for the replacement and renovation ("like to like") of existing assets / total cost of the investement) x 100, during the assessment period | Fi27=(G34/G32)*100 | #DIV/0! | %
Fi28 | Average water charges | Average water charges for direct consumption | Water sales revenue from residential, industrial and other customers (exported water excluded, public water teaxes excluded) / (total authorised - exported water), during the assessment period | Fi28=G36/(A14-A7) | #DIV/0! | EUR/m3
Fi29 |  | Average water charges for exported water | Water sales revenue from exported water (excluding public water taxes)/ exported water, during the assessment period | Fi29=G37/(A5+A7) | #DIV/0! | EUR/m3
Fi30 | Efficiency | Total cost coverage ratio | Total revenues / total costs, during the assessment period | Fi30=G1/G4 | #DIV/0!
Fi31 |  | Operating cost coverage ratio | Total revenues / running costs, during the assessment period | Fi31=G1/G5 | #DIV/0!
Fi32 |  | Delay in accounts receivable | (Accounts receivable from drinking water at the reference date / sales revenues during the assessment period) x assessment period | Fi32=(G38/G3)*H1 | #DIV/0! | days equivalent
Fi33 |  | Investment ratio | Investments subject to depreciation/ depreciation costs, during the assessment period | Fi33=G39/G28 | #DIV/0!
Fi34 |  | Constribution of internal sources to investment | Investments financied by the cash flow / total investement, during the assessment period | Fi34=(G40/G32)*100 | #DIV/0! | %
Fi35 |  | Average age of tangible assets | (Depreciated historical value of tangible assets / historical value of tangible assets) x 100, during the year | Fi35=(G41/G42)*100 | #DIV/0! | %
Fi36 |  | Average depreciation ratio | (Depreciated costs/ historical value of tangible assets) x 100, during the year | Fi36=G28/G42 | #DIV/0!
Fi37 |  | Late payments ratio | [1 - (annual debt from customers / amount billed during the year)], during the year | Fi37=1-(G43/G44) | #DIV/0!
Fi38 |  | Inventory value | Value of overall inventory at the end of the fiscal year / operating revenues during the year | Fi38=G51/G2 | #DIV/0!
Fi39 | Leverage | Debt service coverage ratio | (Cash - flow / financial debt services) x 100, during the assessment period | Fi39=(G45/G46)*100 | #DIV/0! | %
Fi40 |  | Debt equity ratio | Total debt / shareholders' equity, at the end of the fiscal year | Fi40=G47/G48 | #DIV/0!
Fi41 | Liquidity | Current ratio | Current assets / current liabilities, at the reference date | Fi41=G49/G53 | #DIV/0!
Fi42 | Profitability | Return on net fixed assets | [Operating income / (historical value of tangible assets - deprciated historical value of tangible assets)[ x 100, during the year | Fi42=[G54/(G42-G41)]*100 | #DIV/0! | %
Fi43 |  | Return on equity | (Net income (net income after interest payment and taxes) / shareholders' equty) x 100, during the year | Fi43=(G56/G48)*100 | #DIV/0! | %
Fi44 |  | Return on capital employed | [(Operating income (EBIT) - related taxes) / total assets] x 100, during the year | Fi44=[(G54-G55)/G50]*100 | #DIV/0! | %
Fi45 |  | Asset turnover ratio | Sales revenues / total assets, during the year | Fi45=G3/G50 | #DIV/0!
Fi46 | Economic water losses | Non-revenue water by volume | (Non-revenue water / system input volume, during the assessment period) x 100 | Fi46=(A21/A3)*100 | #DIV/0! | %
Fi47 |  | Non-revenue water by cost | (Valuation of non-revenue water components / running costs, during the assessment period) x 100 | Fi47={[(A13+A18)*G57+(A19*G58)]/G5}*100 | #DIV/0! | %

## IWA standard WB
IWA Standard International Water Balance
| Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Revenue Water
(A8)
|  |  | Billed Unmetered Consumption | (A20=A8+A9)
(A10=A8+A9)
(A9)
| (A14=A10+A13) | Unbilled Authorized Consumption | Unbilled Metered Consumption | Non Revenue Water (NRW)
System Input Volume
(A11)
Unbilled Unmetered Consumption
(A3) |  | (A13=A11+A12)
(A12)
| Water Losses | Apparent Losses | Unauthorized Consumption | (A21=A3-A20)
(A16)
Customer Meter Inaccuracies and Data Handling Errors
| (A15=A3-A14) | (A18=A16+A17)
(A17)
Real Losses
(A19=A15-A18)
System Input Volume | Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Revenue Water
(A8)
|  |  | 0 | (A20=A8+A9)
| (A14=A10+A13) | (A10=A8+A9) | Billed Unmetered Consumption | 0
| 0 | 0
(A9)
0
|  | Unbilled Authorized Consumption | Unbilled Metered Consumption | Non Revenue Water (NRW)
(A11)
|  | (A13=A11+A12) | 0
(A3) |  | 0 | Unbilled Unmetered Consumption
0
(A12)
0
| Water Losses | Apparent Losses | Unauthorized Consumption | (A21=A3-A20)
0
|  | (A18=A16+A17) | (A16)
|  | 0 | 0
| (A15=A3-A14) |  | Customer Meter Inaccuracies and Data Handling Errors
0
(A17)
0
Real Losses
(A19=A15-A18)
0

## WB-1stMOD(McKenzie,2007)
1st Modification of IWA Standard International Water Balance (McKenzie, 2007)
System Input Volume | Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Water billed and paid for (Free Basic Recover Revenue) | Revenue Water
(A8)
|  |  | Billed Unmetered Consumption | (A24=A8+A9-A23) | (A24=A8+A9-A23)
|  | (A10=A8+A9) |  | Water billed but NOT PAID for (apparent NRW) | Water which does not generate revenues (TOTAL Non-Revenue Water)
(Α9)
| (A14=A10+A13) |  |  | A23
|  | Unbilled Authorized Consumption | Unbilled Metered Consumption | Water not being sold (Non-Revenue Water/real NRW)
(A11)
(A3) |  | (A13=A11+A12) | Unbilled Unmetered Consumption
|  |  | (A12) |  | (Α23+A21)
| Water Losses | Apparent Losses | Unauthorized Consumption | (A21=A3-A24-A23)
(Α16)
| (A15=A3-A14) | (A18=A16+A17) | Customer Meter Inaccuracies and Data Handling Errors
(A17)
Real Losses
(A19=A15-A18)
System Input Volume | Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Water billed and paid for (Free Basic Recover Revenue) | Water which is sold and generates revenues (is levied)
(A8)
|  |  | 0 | (A24=A8+A9-A23) | (A24=A8+A9-A23)
|  | (A10=A8+A9) | Billed Unmetered Consumption | 0 | 0
|  | 0 |  | Water billed but NOT PAID for (apparent NRW) | Water which does not generate revenues (TOTAL Non-Revenue Water)
(Α9)
| (A14=A10+A13) |  | 0 | A23
| 0 |  |  | 0
|  | Unbilled Authorized Consumption | Unbilled Metered Consumption | Water not being sold (Non-Revenue Water/real NRW)
(A3) |  |  | (A11)
0 |  |  | 0
|  | (A13=A11+A12) | Unbilled Unmetered Consumption
|  | 0 | (A12)
|  |  | 0 | (A21=A3-A24-A23) | (Α23+A21)
| Water Losses | Apparent Losses | Unauthorized Consumption | 0 | 0
(Α16)
|  | (A18=A16+A17) | 0
| (A15=A3-A14) | 0 | Customer Meter Inaccuracies and Data Handling Errors
0
(A17)
0
Real Losses
(A19=A15-A18)
0
Note on F4: ή: Water volume billed and paid by the consumers (Free Basic Recover Revenue)
Note on F7: ή: Water volume billed but never paid by the consumers (apparent NRW)
Note on F11: ή: Water volume unbilled and never paid by the consumers (Non-Revenue Water/reasl NRW)
Note on F26: ή: Water volume billed and paid by the consumers (Free Basic Recover Revenue)
Note on F36: ή: Water volume unbilled and never paid by the consumers (Non-Revenue Water/reasl NRW)
Note on F31: ή: Water volume billed but never paid by the consumers (apparent NRW)

## WB-2ndMOD(Kanakoudis+Tsitsifli)
2nd Modification of IWA Standard International Water Balance (Kanakoudis & Tsitsifli, 2009)
System Input Volume | Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Revenue Water | Water billed and paid for (Free Basic Recover Revenue) | Revenue Water
(A8)
|  |  | Billed Unmetered Consumption | (A20=A8+A9) | (A24=A8+A9-A23) | (A24=A8+A9-A23)
|  | (A10=A8+A9) |  |  | Water billed but NOT PAID for (apparent NRW) | Water billed but NOT PAID for (apparent NRW)
(Α9)
| (A14=A10+A13) |  |  |  | A23 | A23
|  | Unbilled Authorized Consumption | Unbilled Metered Consumption | Non Revenue Water (NRW) | Water not being sold (Non-Revenue Water/real NRW) | Accounted Non Revenue Water
(A11)
(A3) |  | (A13=A11+A12) | Unbilled Unmetered Consumption
|  |  | (A12) | (A21=A3-A20)
| Water Losses | Apparent Losses | Unauthorized Consumption |  | (A21=A3-A24-A23) | (A26=A3-A24-A23-A25)
(Α16)
Customer Meter Inaccuracies and Data Handling Errors
| (A15=A3-A14) | (A18=A16+A17)
(A17)
|  | Real Losses |  |  |  | Water Losses generating revenues (Minimum Charge Difference)
(A19=A15-A18)
A25
System Input Volume | Authorized Consumption | Billed Authorized Consumption | Billed Metered Consumption | Revenue Water | Water billed and paid for (Free Basic Recover Revenue) | Revenue Water
(A8)
|  |  | 0 |  | (A24=A8+A9-A23) | (A24=A8+A9-A23)
|  | (A10=A8+A9) | Billed Unmetered Consumption | (A20=A8+A9) | 0 | 0
|  | 0 |  | 0 | Water billed but NOT PAID for (apparent NRW) | Water billed but NOT PAID for (apparent NRW)
(A9)
|  |  | 0 |  | A23 | A23
| (A14=A10+A13) |  |  |  | 0 | 0
| 0 | Unbilled Authorized Consumption | Unbilled Metered Consumption | Non Revenue Water (NRW) | Water not being sold (Non-Revenue Water/real NRW) | Accounted Non Revenue Water
(A11)
|  | (A13=A11+A12) | 0
|  | 0 | Unbilled Unmetered Consumption
(A3) |  |  | (A12)
0 |  |  | 0 |  |  | (A26=A3-A24-A23-A25)
| Water Losses | Apparent Losses | Unauthorized Consumption | (A21=A3-A20) | (A21=A3-A24-A23) | 0
|  |  |  | 0 | 0
(A16)
|  | (A18=A16+A17) | 0
|  | 0 | Customer Meter Inaccuracies and Data Handling Errors
(A15=A3-A14)
| 0 |  | (A17)
0
|  | Real Losses |  |  |  | Water Losses generating revenues (Minimum Charge Difference)
(A19=A15-A18)
|  | 0 |  |  |  | A25
0